## Audit_Teams_Follow_Up
Team No. | Rig No. | Job Type | Well Name | Field | Closure % | Starting Date | Job Days | Expected Rig
Team_1 | EDC-62 | RA-3 | PTAH-48 | Kalabsha | 44 | 2023-08-12 | 5 | EDC-48
Team_2 | EDC-92 | RA-3 | MENES-58 | Menes | 55 | 2023-08-13 | 3 | Home
Team_3 | EDC-40 | FCS-1 | BRIDGE 1-X | Zarif | 60 | 2023-08-13 | 7 | Home

## Drops_Teams_Follow_Up
Team No. | Rig No. | Campaign No. | Last Campaign | Mast Availability | Non Availability Reasons | Well Name | Field
Team_1 | Home | ### | ### | ### | ### | ### | ###
Team_2 | Home | ### | ### | ### | ### | ### | ###
Team_3 | EDC-40 | 1st | 2023-08-13 | Ok | No Reasons | BRIDGE 1-X | Zarif

## Critical_Points_Follow_Up
Rig_No. | No. | Location | Description | Priority | Ref. | Final_ Status | Phase
EDC-62 | 3.2.13 | Single Ram | SGL ram was found expired, required to be replaced with new SGL certified, MFD 18 Feb. 2018. | Critical | IADC, API RP53, API RP54, API 16D, API RP16E, API 16A | Open | FCS-3
EDC-62 | 4.2.14 | SCR | While power limit test ,Generator#2 load reaching 1750amp over 100% from generator current, Power limit not indicate . (The Power Limit Circuit prevents the load from exceeding the capacity of engines on line). | Critical | OEM | In progress | FCS-3
EDC-62 | 4.2.28 | MCC | Found Clear AC Ground Fault in MCC , need to find the defected grounded equipment and clear the fault ASAP | Critical | OEM/PMS | Open | FCS-3
EDC-40 | 4.8.1 | Diesel Tank | Fuel Purifier AC motor is not Explosion Proof type need to be replaced by EX type motor. | Critical | API RP 500 8.2.1.4 , API RP 14FZ , IADC HSE Guide Lines , IEC 60079 | Open | FCS-1
EDC-40 | 5.8.1 | Diesel Fire Pump | The diesel Fire Pump is not in working order, which is required to be ready and in working order ASAP. | critical | API RP54 7.2.2 IADC HSE Reference Guide NFPA 20 | open | FCS-1